## Report Summary
Field | Value
Report Title | new report for edan
Description | kdlajdlda dnlaks jc;asjlf aljdals
Project | Electrical & Energy-Loss Risk Assessment
Project Reference | ZSP-000001
Client | ZORAYS KHALID
Site | Main Industrial Facility
Location | 56 K ST 3 PHASE 5 DHA LAHORE
System Capacity (kW)
Project Status | active
Overall Progress | 7%
Rectification Progress | 7%
Evidence Progress | 7%
Testing Progress | 0%
Action Plan Progress | 0%
Total Tasks | 15
In Progress | 14
Complete | 1
Before Evidence | 1
After Evidence | 1
Completion Percentage | 6.67%
Generated At | 2026-08-12 10:40

## Task Register
Sr. No. | Description | Before Picture | After Picture | Complete | In Progress
1 | Panel door locks are damaged, allowing rainwater to enter the panel. |  |  | ✓
2 | Component rating does not comply with the approved Single Line Diagram (SLD). |  |  |  | ✓
3 | Breaker or single-pole MCB is faulty and requires replacement. |  |  |  | ✓
4 | Earth Leakage Circuit (ELC) protection is not installed. |  |  |  | ✓
5 | Neutral link is open/loose, resulting in unintended current flow. |  |  |  | ✓
6 | Busbar is corroded and overheating, creating a potential risk of sparking. |  |  |  | ✓
7 | Red and Yellow phase cables are undersized and do not meet the required current rating. |  |  |  | ✓
8 | Push button is faulty, due to which the circuit has been connected in bypass mode. |  |  |  | ✓
9 | Overload protection ratings are mismatched, causing circuit and load imbalance. |  |  |  | ✓
10 | DOL starter and timer are bypassed, with the circuit connected directly. |  |  |  | ✓
11 | Selector switches are faulty and require repair or replacement. |  |  |  | ✓
12 | Terminal block requires replacement. |  |  |  | ✓
13 | Basement Entrance Right – Ground Floor DB-01. |  |  |  | ✓
14 | AC drain water is directly entering the DB, causing an earth leakage fault and resulting in smoke from the DB. |  |  |  | ✓
15 | MCB breaker is faulty and requires replacement. |  |  |  | ✓

## Evidence Register
Sr. No. | Evidence Type | Image Path | Preview
1 | Before | /uploads/tasks/before/before-6a7c0ae31495acc93fcd1315-1786531137125-8caba386702d4f718800335c26a33068.jpg
1 | After | /uploads/tasks/after/after-6a7c0ae31495acc93fcd1315-1786531154787-77c914643c744c0ba24aa07f2514234d.png