# ZSP-000001 — Electrical & Energy-Loss Risk Assessment

Electrical & Energy-Loss Risk Assessment | ZSP-000001

# Project Details

Project: Electrical & Energy-Loss Risk Assessment

Project Reference: ZSP-000001

Client: ZORAYS KHALID

Site: Main Industrial Facility

Location: 56 K ST 3 PHASE 5 DHA LAHORE

Project Status: active

Start Date: 26 Jul 2026

Expected Completion: 26 Oct 2026

Overall Progress: 4%

Rectification: 0% | Evidence: 7% | Testing: 0% | Action Plan: 0%

# Report Summary

| Total Tasks | In Progress | Complete | Before Evidence | After Evidence | Completion |
| --- | --- | --- | --- | --- | --- |
| 15 | 15 | 0 | 1 | 1 | 0% |

# Task Register

| Sr. No. | Description | Before | After | Status |
| --- | --- | --- | --- | --- |
| 1 | Panel door locks are damaged, allowing rainwater to enter the panel. | 1 | 1 | In Progress |
| 2 | Component rating does not comply with the approved Single Line Diagram (SLD). | 0 | 0 | In Progress |
| 3 | Breaker or single-pole MCB is faulty and requires replacement. | 0 | 0 | In Progress |
| 4 | Earth Leakage Circuit (ELC) protection is not installed. | 0 | 0 | In Progress |
| 5 | Neutral link is open/loose, resulting in unintended current flow. | 0 | 0 | In Progress |
| 6 | Busbar is corroded and overheating, creating a potential risk of sparking. | 0 | 0 | In Progress |
| 7 | Red and Yellow phase cables are undersized and do not meet the required current rating. | 0 | 0 | In Progress |
| 8 | Push button is faulty, due to which the circuit has been connected in bypass mode. | 0 | 0 | In Progress |
| 9 | Overload protection ratings are mismatched, causing circuit and load imbalance. | 0 | 0 | In Progress |
| 10 | DOL starter and timer are bypassed, with the circuit connected directly. | 0 | 0 | In Progress |
| 11 | Selector switches are faulty and require repair or replacement. | 0 | 0 | In Progress |
| 12 | Terminal block requires replacement. | 0 | 0 | In Progress |
| 13 | Basement Entrance Right – Ground Floor DB-01. | 0 | 0 | In Progress |
| 14 | AC drain water is directly entering the DB, causing an earth leakage fault and resulting in smoke from the DB. | 0 | 0 | In Progress |
| 15 | MCB breaker is faulty and requires replacement. | 0 | 0 | In Progress |