# ZSP-000001 — Electrical & Energy-Loss Risk Assessment

Electrical & Energy-Loss Risk Assessment | ZSP-000001

# Project Details

Project: Electrical & Energy-Loss Risk Assessment

Project Reference: ZSP-000001

Client: ZORAYS KHALID

Site: Main Industrial Facility

Location: 56 K ST 3 PHASE 5 DHA LAHORE

Project Status: active

Start Date: 26 Jul 2026

Expected Completion: 26 Oct 2026

Overall Progress: 4%

Rectification: 4% | Evidence: 4% | Testing: 0% | Action Plan: 0%

# Report Summary

| Total Tasks | In Progress | Complete | Before Evidence | After Evidence | Completion |
| --- | --- | --- | --- | --- | --- |
| 51 | 49 | 2 | 2 | 2 | 3.92% |

# Task Register

| Sr. No. | Description | Before | After | Status |
| --- | --- | --- | --- | --- |
| 1 | Panel door locks are damaged, allowing rainwater to enter the panel. | 1 | 1 | Complete |
| 2 | Component rating does not comply with the approved Single Line Diagram (SLD). | 1 | 1 | Complete |
| 3 | Breaker or single-pole MCB is faulty and requires replacement. | 0 | 0 | In Progress |
| 4 | Earth Leakage Circuit (ELC) protection is not installed. | 0 | 0 | In Progress |
| 5 | Neutral link is open/loose, resulting in unintended current flow. | 0 | 0 | In Progress |
| 6 | Busbar is corroded and overheating, creating a potential risk of sparking. | 0 | 0 | In Progress |
| 7 | Red and Yellow phase cables are undersized and do not meet the required current rating. | 0 | 0 | In Progress |
| 8 | Push button is faulty, due to which the circuit has been connected in bypass mode. | 0 | 0 | In Progress |
| 9 | Overload protection ratings are mismatched, causing circuit and load imbalance. | 0 | 0 | In Progress |
| 10 | DOL starter and timer are bypassed, with the circuit connected directly. | 0 | 0 | In Progress |
| 11 | Selector switches are faulty and require repair or replacement. | 0 | 0 | In Progress |
| 12 | Terminal block requires replacement. | 0 | 0 | In Progress |
| 13 | Basement Entrance Right – Ground Floor DB-01. | 0 | 0 | In Progress |
| 14 | AC drain water is directly entering the DB, causing an earth leakage fault and resulting in smoke from the DB. | 0 | 0 | In Progress |
| 15 | MCB breaker is faulty and requires replacement. | 0 | 0 | In Progress |
| 16 | AC drain water has damaged the DB’s LDR, causing the dusk controller to malfunction. | 0 | 0 | In Progress |
| 17 | Cable dressing and proper cable management are required. | 0 | 0 | In Progress |
| 18 | MCB breaker is faulty and requires replacement. | 0 | 0 | In Progress |
| 19 | Ground plate is missing and needs to be installed. | 0 | 0 | In Progress |
| 20 | DB door is damaged and requires repair or replacement. | 0 | 0 | In Progress |
| 21 | Overload relay is burnt, and its tripping time is excessively high. | 0 | 0 | In Progress |
| 22 | Basement Entrance Left Side – Ground Floor DB. | 0 | 0 | In Progress |
| 23 | Electrical connections are loose and require proper tightening. | 0 | 0 | In Progress |
| 24 | Cable is overheating and requires inspection and rectification. | 0 | 0 | In Progress |
| 25 | AC drain water is entering the DB, creating a potential electrical and safety hazard. | 0 | 0 | In Progress |
| 26 | MCB is hanging unsecured and requires proper mounting and fixing inside the DB. | 0 | 0 | In Progress |
| 27 | DOL starter is bypassed, and the circuit is connected directly. | 0 | 0 | In Progress |
| 28 | Temporary electrical connection is being used. | 0 | 0 | In Progress |
| 29 | Basement Back Entrance Side – Ground Floor DB. | 0 | 0 | In Progress |
| 30 | Cable dressing and proper cable management are required. | 0 | 0 | In Progress |
| 31 | Cable joints are present inside the drain area and require proper rectification. | 0 | 0 | In Progress |
| 32 | Terminal block is melted and requires replacement. | 0 | 0 | In Progress |
| 33 | Electrical connections are loose and require proper tightening. | 0 | 0 | In Progress |
| 34 | Overload relay timing is set at the maximum setting of 05 and requires proper adjustment. | 0 | 0 | In Progress |
| 35 | Electrical load is unbalanced and requires proper load balancing. | 0 | 0 | In Progress |
| 36 | Cable dressing and proper cable management are required. | 0 | 0 | In Progress |
| 37 | Cables are causing current leakage to the equipment body, creating an electrical safety hazard. | 0 | 0 | In Progress |
| 38 | Cable sizes are undersized and do not meet the required current-carrying capacity. | 0 | 0 | In Progress |
| 39 | Water has accumulated inside the DB cable conduits/pipes, creating an electrical safety hazard. | 0 | 0 | In Progress |
| 40 | AC drain water is falling directly onto the DB, creating a potential electrical and safety hazard. | 0 | 0 | In Progress |
| 41 | Main Feeder Panel – Near Masjid. | 0 | 0 | In Progress |
| 42 | All DBs are connected through loop connections and require proper inspection and rectification. | 0 | 0 | In Progress |
| 43 | DB has an earth fault/short circuit to ground and requires immediate rectification. | 0 | 0 | In Progress |
| 44 | CTs (Current Transformers) are installed but are not connected/in use. | 0 | 0 | In Progress |
| 45 | Terminal blocks are melted and require replacement. | 0 | 0 | In Progress |
| 46 | Magnetic contactors are faulty and require replacement. | 0 | 0 | In Progress |
| 47 | An open-circuit/bypassed connection is being used and requires proper rectification. | 0 | 0 | In Progress |
| 48 | Voltmeter and ammeter are missing and need to be installed. | 0 | 0 | In Progress |
| 49 | Foundation Pump – Electrical connections are loose and require proper tightening. | 0 | 0 | In Progress |
| 50 | An open-circuit bypass connection is being used and requires proper rectification. | 0 | 0 | In Progress |
| 51 | LT Room – Lighting DB. | 0 | 0 | In Progress |